Connect power to the Timer Controller.

The LCD Display has three display modes – Power Up, Counter & Timer, and Totalizer. 

To Change Display Modes
			Press and hold PGRM key. 
			Display will toggle every 3 seconds to next mode
			Release PGRM key at desired mode

--------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

1. Power Up Mode - Displays support parameters(serial#, model#, phone#, mfg.date) and also some operating parameters
 that are user programmable (Timing-Min/Sec, Sequential-On/Off, Totalizer setup – (Program display to  
 match your meter output settings).

			-------------------------------------------------------------------------------------------------------------------------------------------------
			Press PGRM key momentarily and repeatedly to scroll through and view these parameters quickly.    
			Otherwise, Program display will scroll automatically.
			Program blinking parameters to desired values with the INCR or DECR keys.

			-------------------------------------------------------------------------------------------------------------------------------------------------
			To exit Power Up Mode press and hold PGRM key for approximately 3 seconds.
			Display will advance to Counter & Timer mode.

--------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

2. Counter & Timer Mode -  Displays Counters and Timers and their status (on/off, time remaining)

			To Program Counters and Timers
			Press PGRM key momentarily.  A blinking arrow will appear pointing at C1(Counter 1)
			Press INCR or DECR keys momentarily and repeatedly to adjust value.  Press PGRM key to advance to T1(Timer 1).
			Repeat above steps for counters C2 and Timer T2 if applicable.
			For FAST set, press and hold INCR or DECR keys. After five counts, digits will change rapidly.
					
Example:  	100 Gallons of make-up water before starting feed and bleed cycle for 10 seconds, with meter 
		pulse rate output of 10 GPC (Gallons Per Contact).
 		Divide meter pulse rate (10) into 100 gallons = 10 for counter setting.
		Pump output of 10 seconds = 10 for timer setting.

			-------------------------------------------------------------------------------------------------------------------------------------------------
			To exit Counter & Timer Mode press and hold PGRM key for approximately 3 seconds.
			Display will advance to Totalizer mode.

--------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------------

3. Totalizer Mode -   Displays total counts received(switch closures) from the water meter.  This provides total or individual historical values 
 based on the user’s preference.  No action required to record total input counts received.

			--------------------------------------------------------------------------------------------------------------------------------------------------
			To Adjust Totalizer:
			Press PGRM key momentarily and repeatedly until desired digit blinks.
			Press INCR or DECR keys to adjust value.

			-------------------------------------------------------------------------------------------------------------------------------------------------
			To Clear Totalizer :
			Press and hold INCR and DECR keys simultaneaously

			--------------------------------------------------------------------------------------------------------------------------------------------------
			To exit Totalizer Mode press and hold PGRM key for approximately 3 seconds.
			Display will advance to Power Up Mode.

			--------------------------------------------------------------------------------------------------------------------------------------------------

Operate Feed Pump Controller
Unit is now ready to operate.  
Replace dust cover.  
When programmed number of input signals arrives from the water meter to the counter(s), the timer(s) will be activated.